## Slide 1
Energy Web Server
User Manual
06/22-01
RA00161CH

## Slide 3
Contents
1. Licence Agreements 5
2. System requirements 7
3. Catalogue numbers 7
4. Compatible Devices 8
4.1 Measuring / metering devices 8
5. Languages available 11
6. Preliminary operations 12
7. Implementation 12
7.1 Local settings 12
7.2 Connecting the device to a PC - Programming 12
7.3 Web Server default settings 12
7.4 LAN configuration of the computer 13
7.5 Configuration of the Web Server 15
7.5.1 Network settings - Personal configuration 15
7.5.2 Access with new Network parameters 18
7.6 Date and Time settings 21
7.7 Update of the Web Server 23
7.7.1 Update procedure 24
7.8 Changing of the Web Server’s language 25
7.8.1 Changing of the default language 25
7.8.2 Changing of the display language 26
7.9 Remote settings 27
7.10 Connection schemes - Normal Use 27
7.11 LAN configuration of the computer - Automatic IP address 28
7.12 Configuration of the electric installation in the Web Server - “System configuration” 30
7.12.1 Gateways and Devices configuration 32
7.12.1.1 Creating and Saving new Gateways 33
7.12.1.2 Creating and Saving of “Physical” Devices 34
7.12.1.3 Advanced options 39
7.12.1.4 System functions 42
7.12.2 Loads, Groups and Panel boards configuration 44
7.12.2.1 Panel boards 45
7.12.2.2 Loads 46
7.12.2.3 Measure groups 47
7.12.2.4 System functions 48
7.12.3 Bill of Consumptions 50
7.12.3.1 Creating and Saving Tariffs and new Cost Rules 51
7.12.4 Configuration of the data sample rate 57
7.12.5 Master/Slave function 59
7.12.5.1 Activation of the function 60
7.12.5.2 Creating and Saving of “Virtual” Gateways and Devices 61

## Slide 4
Contents
8. Use 65
8.1 Access 65
8.1.1 Access rights 65
8.1.2 Creating a new User 66
8.1.3 Changing of the access rights 67
8.1.4 Logout procedure 68
8.2 Data display pages 69
8.2.1 My panel board 69
8.2.2 Consumptions: data & diagrm. 72
8.2.2.1 Grand Total 74
8.2.2.2 Partials - Groups and load type 76
8.2.2.3 Compare 77
8.2.2.4 Details 78
8.2.2.5 Tariffs 80
8.2.2.5.1 Total 81
8.2.2.5.2 Details 82
8.2.2.6 Advanced histograms and charts display 83
8.2.3 Link Functionality 86
8.3 Historical of consumptions 88
8.3.1 CSV files options 88
8.3.2 Access to CSV files 89
8.3.3 Management of CSV files 91
8.3.3.1 “devices“ folder 92
8.3.3.2 “energy“ folder 93
8.3.3.3 “eqcheck“ folder 93
8.3.3.4 “gas“ folder 93
8.3.3.5 “overall total“ folder 93
8.3.3.6 “settings“ folder 94
8.3.3.7 “water“ folder 94
8.4 Reports & data download 95
8.4.1 Data download 95
8.4.2 Reports 99
8.5 Pushing e-mail and notifications 103
8.5.1 E-mail settings 103
8.5.2 Telegram 105
8.5.3 Automatic reports 107
8.5.4 Alerts settings 110
8.6 Reports: alarms 112
8.7 System information 113
9. Backup and Restore 115
9.1 Backup procedure 115
9.2 Restore procedure 117
10. Network type and access mode 119
10.1 LAN/Intranet 119
10.1.1 Ports 119
10.2 WAN/Internet 120
10.2.1 Ports 121
11. FAQ 122
11.1 Access problems 122
11.2 Telegram problems 122
11.3 E-mails sending test problems 122

## Slide 5
1. License Agreements
IMPORTANT:
PLEASE READ THE TERMS AND CONDITIONS OF THIS LICENSE AGREEMENT CAREFULLY BEFORE USING THE SOFTWARE (AS DEFINED BELOW).
THIS IS A LICENSE AGREEMENT BETWEEN YOU AND BTicino SpA (BTicino) WHICH IS LOCATED IN VIALE BORRI 231, 21100 VARESE, ITALY.
BY OPENING THIS PACKAGE, BREAKING THE SEAL, CLICKING THE “I AGREE” OR “YES” BUTTON OR OTHERWISE INDICATING ASSENT ELECTRONICALLY, OR LOADING THE SOFTWARE, YOU AGREE TO THE TERMS AND CONDITIONS OF THIS LICENSE AGREEMENT.
IF YOU DO NOT AGREE TO THESE TERMS AND CONDITIONS, MAKE NO FURTHER USE OF THE SOFTWARE, AND CONTACT YOUR VENDOR OR BTicino CUSTOMER SERVICE FOR INFORMATION ON HOW TO OBTAIN A REFUND OF THE MONEY YOU PAID FOR THE SOFTWARE.
1. DEFINITIONS
“Software” means:
(a) all of the contents of the files of the software (“Energy Management Software”) either with a Web server (“Energy Web Server”);
(b) related explanatory written materials or files (“Documentation”), fonts and the packaging of the product;
(c) upgrades, modified versions, updates, additions, and copies of the foregoing, provided to you by BTicino at any time (collectively, “Updates”).
“Use” means to access, install, download, copy, or otherwise benefit from using the functionality of the Software.
2. GENERAL USE OF THE SOFTWARE
2.1 License
This contract is a license Agreement.
BTicino grants you a right not exclusive and not transferable to use the Software according to the conditions ant terms defined below.
2.2 Rights and obligations
You may:
- use one copy of the Software on a single computer. If a greater number of copies and/or number of computers is specified within the Documentation or the applicable transaction documentation from the authorized distributor or reseller from which you obtained the Software, you may use the Software in accordance with such specifications;
- make one copy of the Software for back-up or archival purposes, or copy the Software onto the hard disk of Your computer and retain the original for back-up or archival purposes;
- use the Software on a network, provided that you have a licensed copy of the Software for each computer that can access the Software over that network;
- permanently transfer all of your rights in the Software granted under this License Agreement to another person or entity, provided that you retain no copies of the Software and the transferee agrees to the terms of this License Agreement. Partial transfer of your rights under this License Agreement shall not be permitted. For example, if the applicable documentation grants you the right to use multiple copies of the Software, only a transfer of the rights to use all such copies of the Software would be valid;

## Slide 6
1. License Agreements (continued)
2.2 Rights and obligations (continued)
- use the Software in accordance with any additional permitted uses which may be set forth below.
You may not, nor may you permit any other person to:
- sublicense, rent or lease any portion of the Software;
- reverse engineer, decompile, disassemble, modify, translate, make any attempt to discover the source code of the Software or create derivative works from the Software;
- use the Software as part of a facility management, timesharing, service provider or service bureau arrangement;
- use the Software in any manner that is not permitted pursuant to this License Agreement.
3. COPYRIGHT
The Software is the property of BTicino or his licensers and is protected by law.
4. LIMITED WARRANTY
Warranty period for Products shall be 12 (twelve) months from delivery date.
BTicino guarantees the smooth running of this software only with the use of products BTicino. He cannot be held responsible in case of malfunction due to the use of products others than products BTicino.
5. LIMITATIONS OF LIABILITY
BTicino cannot be held liable for any damages of any kind, including without limitation any consequential, operating loss, data loss, malfunction of other softwares installed on your computer or any lost profits resulting of the impossibility to use the software, even if BTicino has been aware of the possibility of such damage.
6. TERMINATION
BTicino has the right to terminate this Agreement by rights immediately by a written notification if you fail to comply with any term of this Agreement and in particular with the provision of article 2.2.
Upon termination of the license, you accept to destroy all copies of the Software and his Documentation.
7. GOVERNING LAW
This Agreement will be governed by Italian Law.
In the event of issues relating to the construction, validity and/or execution of this agreement the Parties undertake to find an amicable settlement.
Failing such a settlement, the disputes shall be submitted to the exclusive jurisdiction of the Court of Milan.

## Slide 7
2. System requirements
Display possible on:
  PC: (Device, Web Browser)
  Firefox : version 50 and following (v50.0+)
  Chrome : v55.0+
  Safari : v10.0+
  Opera : v53.0+
  Tablet: (Device, Operating system, Web Browser)
    iPad (all versions), iOS 10+, Safari
    Android v6.0+, Chrome v55.0+
  Smartphones: (see User Guide)
3. Catalogue numbers
SXWS255: “Energy Web Server 255”
  Management up to 255* devices
    Note: for each Gateway max. 32 Modbus addresses or 32 pulse counters
      * Recommended value 128
    Software version 3.10.0

## Slide 8
    4. Compatible devices
    4.1 Measuring / metering devices
  Range NEMO
    Multifunction measuring units RS485 :
      Nemo D4-L, Cat.No MF6FT40026
      Nemo D4-L +, Cat.Nos MF6HT40003, MF6HT40006, MF6HT4000H
      Nemo D4-e, Cat.No MFD4E06
      Nemo D4-Le, Cat.Nos MFD4421, MFD4422, KRNEMOD4LE080, KRNEMOD4LE142, KRNEMOD4LE190
      Nemo D4-Dc, Cat.Nos MF6DC4200H, MF6DC42006, MF6DC4206H, MF6DC42066
      Nemo D4-EC, Cat.Nos MKD4R63DT, MKD4R125DT, MFD4ORFCDT1, MFD41ORFCDT, MFD42ORFCDT
      Nemo 72-Le, Cat.Nos MF72421, MF72422
      Nemo 96HD-e, Cat.No MF96E06
      Nemo 96HD-Le, Cat.Nos MF96411 + IF96001, MF96412 + IF96001, MF96411 + IF96012, MF96412 + IF96012, MF96421, MF96422, KRNEMOHDLE080, KRNEMOHDLE142, KRNEMOHDLE190
      Nemo 96HD, Cat.Nos MF96001 + IF96001, MF96002 + IF96001, MF96001 + IF96012, MF96002 + IF96012
      Nemo 96HD+, Cat.Nos MF96021 + IF96001, MF96022 + IF96001, MF96021 + IF96012, MF96022 + IF96012
      Nemo 96EA, Cat.Nos MFQ96021 + IF96001, MFQ96022 + IF96001
      Nemo 96-EC, Cat.Nos MK96R63DT, MK96R125DT, MF96ORFCDT1, MF961ORFCDT, MF962ORFCDT
    Multifunction measuring units pulse output (via the Pulse Concentrators Cat.Nos IF4C001* or SXMIMP* or pulse input of Energy counters Cat.Nos CE2DF3DTCL1*, CE4DF3DTCL1* and CE4TBDTCL1*):
      Nemo D4-L +, Cat.Nos MF6HTU0003, MF6HTU0006, MF6HTU000H
      Nemo D4-Le, Cat.Nos MFD4411, MFD4412
      Nemo 72-Le, Cat.Nos MF72411, MF72412
      Nemo 96HD-Le, Cat.Nos MF96411, MF96412

## Slide 9
    4.1 Measuring / metering devices (continued)
    Range CONTO
    Energy counters RS485:
      Conto D1, Cat.No CE11165A4
      Conto D2, Cat.Nos CE20195A4, CE2DF3DTCL1
      Conto D2 MID, Cat.Nos CE2DMID11, CE2DF3DTMID
      Conto D4-Pd, Cat.Nos CE4DT06A4, CE4DF3DTCL1
      Conto D4-Pd MID, Cat.Nos CE4DMID31, CE4DF3DTMID
      Conto D4-Pt, Cat.Nos CE4DT12A4, CE4DT12A6, CE4DT14A4, CE4DT14A6, CE4TBDTCL1
      Conto D4-Pt MID, Cat.Nos CE4DMID01, CE4TBDTMID
      Conto D6-Pd, Cat.No CE6DT1256
      Conto D6-Pd MID, Cat.No CE6DMID56
    Energy counters pulse output (via the Pulse Concentrators Cat.Nos IF4C001* or SXMIMP* or pulse input of Energy counters Cat.Nos CE2DF3DTCL1*, CE4DF3DTCL1* and CE4TBDTCL1*) :
      Conto D1, Cat.No CE11165A2
      Conto D1 MID , Cat.No CE1DMID12
      Conto D2, Cat.Nos CE20195A2, CE2DF30PCL1
      Conto D2 MID, Cat.Nos CE2DMID12, CE2DF30PMID
      Conto D4-Pd, Cat.Nos CE4DT06A2, CE4DT06A23F, CE4DF30PCL1
      Conto D4-Pd MID, Cat.Nos CE4DMID22, CE4DMID32, CE4DF30PMID
      Conto D4-Pt, Cat.Nos CE4DT12A2, CE4DT14A2, CE4TB0PCL1
      Conto D6-Pd, Cat.No CE6DT1252
      Conto D6-Pd MID, Cat.No CE6DMID52

## Slide 10
  4.1 Measuring / metering devices (continued)
  Range NEMO SX
    Multifunction measuring devices:
      Single-phase connection via Closed Rogowski coil(s) – Cat.Nos SX3M63 and SXMM63
      Three-phase connection via Closed Rogowski coil(s) – Cat.Nos SXMT63 and SXMT125
      Single-phase or Three-phase (configurable) connection with CT - Cat.No SXMMT5
      Three-phase connection via Open Flexible Rogowski coils - Cat.Nos SXMR02, SXMR04, SXMR06 and SXMR08
    State and Control modules:
      Multifunction State Module - Cat.No SXMC02
      Multifunction Control Module - Cat.No SXM0C1
      via Modbus/NEMO SX interface - Cat.No SXI485
  Gas counters
    Any device with pulse output via the Pulse Concentrators Cat.Nos IF4C001* or SXMIMP* or pulse input of Energy counters Cat.Nos CE2DF3DTCL1*, CE4DF3DTCL1* and CE4TBDTCL1*
  Water counters
    Any device with pulse output via the Pulse Concentrators Cat.Nos IF4C001* or SXMIMP* or pulse input of Energy counters Cat.Nos CE2DF3DTCL1*, CE4DF3DTCL1* and CE4TBDTCL1*
  * Note: Pulse Concentrator and Energy counters with pulse input must be properly programmed to be compatible with the type of counter (Refer to the technical documentation of each device)
  Range Power factor controller ALPTEC
    ALPTEC3.2 + ExtRS485
    ALPTEC5.2 + ExtRS485
    ALPTEC8.2 + ExtRS485
    ALPTEC8 + ExtRS485
  “Generic” Measurement/Counting Devices with Modbus RS485 output
  Any “other manufacturers” meter or counter with Modbus RS485 output, limited only to positive active energy

## Slide 11
      5. Languages available
Languages:
  中国
  Deutsch
  English
  Español
  Français
  Français (Belgique)
  Ελληνικά
  Italiano
  Nederlands (Belgïe)
  Nederlands
  Polski
  Portuguese
  Русский

## Slide 12
6. Preliminary operations
ATTENTION!
Before commissioning the installation we recommend you to verify on the IME “e-catalogue” site if a software update is available.
Download the update file from IME site to your computer. This file will be used to update the firmware.
(After downloading the update file follow the procedure detailed on pages 21 to 22 of this manual)
7. Implementation
7.1 Local settings
Local settings / configuration
Procedure to configure the Web Server from a computer directly connected to it.
Materials required
Web Server’s instruction sheet
Web Server’s user manual
PC with a web browser (Chrome, Firefox, etc.)
Note: The local settings must be made ​mandatorily by a computer
Useful Information
IP network parameters for Web Server (use the Parameters Table of the Web Server )
7.2 Connecting the device to a PC - Programming
Connect the Web Server directly to a PC by the Ethernet cable (is possible to pass through a switch)
Note: In this phase don’t connect the Web Server to other devices (Gateways, etc. ) or to the Building Network
Supply the Web Server
7.3 Web Server default settings
IP Address: 192.168.1.100
Subnet Mask: 255.255.255.0
Default Gateway: 192.168.1.1
Note: Web Server and Gateway have the same default settings
Building
Network


Hub/ Switch

## Slide 13
7.4 LAN configuration of the computer
Follow the procedure:
1. In the Start menu choose “Settings” then click “Network Connections”
2. Click “Local Area Connection”
3. Click “Properties”
3
1
2

## Slide 14
4. Click “Internet Protocol (TCP/IP)”
5. Click “Properties”
6. Click “Use the following IP address”
7. Enter the LAN parameters as shown
8. Click “OK” to confirm
9. Click “OK” to confirm
9
4
6
5
8
7

## Slide 15
7.5 Configuration of the Web Server
7.5.1 Network Settings - Personal configuration
To access to the Web Server, type the IP address 192.168.1.100 (default IP)
in the web browser.
Web Server’s Login page appears
1. Type the access PIN code 99999 (default PIN)
2. Click “OK”
3. Type the access PUK code 00000 9999 00000 (default PUK)
4. Click “OK”
Web Server’s Home page appears.
IP
2
1
3
4

## Slide 16
5. Click “Web Server configuration”
6. Click “Web server settings”
7. Click “Network settings” to configure the LAN properties of the Server
5
7
6

## Slide 17
8. Enter the new LAN settings.
Example of IP network settings to configure on the Web Server
  IP Address: 172.168.1.101
  Subnet mask: 255.255.255.0
  Default gateway: 172.168.1.1
9. Click “Save” 2 times to confirm
Note: Now the Web server has new network parameters
8
9

## Slide 18
7.5.2 Access with new Network parameters
After changing of the Network parameters of the Server, it is necessary to configure manually an IP address compatible with the new IP address of the web server as shown below: (in the example the server has the IP 172.168.1.101  use 172.168.1.99)
1. In the Start menu choose “Settings” then click “Network Connections”
2. Click “Local Area Connection”
3. Click “Properties”
3
1
2

## Slide 19
4. Click “Internet Protocol (TCP/IP)”
5. Click “Properties”
6. Click “Use the following IP address”
7. Enter the LAN parameters as shown
8. Click “OK” to confirm
9. Click “OK” to confirm
9
4
6
5
8
7

## Slide 20
To access to the Web Server, type the new IP address 172.168.1.101 (in the example) in the web browser.
Web Server’s Login page appears
1. Type the access PIN code 99999 (default PIN)
2. Click “OK”
3. Type the access PUK code 00000 9999 00000 (default PUK)
4. Click “OK”
Web Server’s Home page appears.
IP
2
1
4
3

## Slide 21
7.6 Date and Time settings
In the Web Server’s Home page
1. Click “Web Server configuration
2. Click “Web server settings”
3. Click “Date and Time” to set these parameters
1
3
2

## Slide 22
4. Enter the new parameters
Time zone
Data and time
5. Click “Save” to confirm
Alternatively, you can use the “Automatic time settings” function that allow the Web Server reach the clock from a Network time protocol (NTP) Server.
6. Click to enable (ON) “Automatic time settings”.
7. It is possible to set: - the IP address of an internal NTP server, if the Web server is connected to an intranet that doesn’t allow Internet connection - the address of a public NTP server, if the Web server is connected to Internet (e.g. of an European public NTP server: 0.europe.pool.ntp.org)
8. Click “Save” to confirm
Note: To get correct Date & Time using the “Automatic time settings”, is fundamental to set the correct Time zone.
4
5
6
7
8

## Slide 23
7.7 Update of the Web Server
Materials required:
File downloaded from the IME “e-catalogue”:
  Energy_Manager_Web_Server_SXWS10_32_255_v_r_b.zip
Energy_Manager_Web_Server = Product Name
SXWS10_32_255 = Catalog numbers
v_r_b = Version of the embedded application
The folder .zip contains the following files:
File “.jar”: web server’s update package
Procedure for updating the Web Server: follow the procedure
Access to the Web server typing PIN and PUK codes
Web Server’s home page appears
1. Click “Web Server configuration”
2. Click “Software update”
1
2

## Slide 24
Compare the version of the installed software with the version of the file received from technical customer service. Update the Software if the file version is more recent than the installed version.
7.7.1 Update procedure
From the compressed folder, extract on your computer the file:
“wsmeasure.jar” Note: Web server automatically recognizes the type of license.
In the “Software update” page
1. Click “Browse” to select the file “.jar” from your computer
2. Click “Upgrade”
IMPORTANT: please allow the time for the updating procedure: about 30 seconds
Verify that the update has been done checking the software version on the “Software’s update” page
1
2

## Slide 25
7.8 Changing of the Web Server’s language
7.8.1 Changing of the default language
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Web server settings”
3. Click “CSV and other settings”
1
3
2

## Slide 26
4. Choisir la langue parmi la liste des langues
5. Cliquer sur “Sauvegarder” pour confirmer
Note: la langue sera changée à la prochaine connexion.
7.8.2 Changing of the display language
In the Web Server’s Home page
1. Choose the proper language from the list box.
Note: this operation doesn’t change the default language.
5
4
1

## Slide 27
7.9 Remote settings
Settings / configurations of the electrical installation
Procedure to configure the different devices on the web server
Materials required
Web Server’s user manual
A computer with a web browser (Chrome, Firefox, etc.)
Useful Information
Network and RS485 bus parameters for Gateways and Devices (use the Parameters Table of the Web Server)
7.10 Connection schemes - Normal Use
Building
Network

## Slide 28
7.11 LAN configuration of the computer - Automatic IP address
Follow the procedure:
1. In the Start menu choose “Settings” then click “Network Connections”
2. Click “Local Area Connection”
3. Click “Properties”
3
1
2

## Slide 29
4. Click “Internet Protocol (TCP/IP)”
5. Click “Properties”
6. Click “Obtain an IP address automatically”
7. Click “OK” to confirm
8. Click “OK” to confirm
8
4
6
5
7

## Slide 30
7.12 Configuration of the electric installation in the Web Server - “System configuration”
Type the set IP address in the web browser.
Web Server’s login page appears
1. Type an access PIN code (ex. 99999 - default PIN)
2. Click “OK”
3. Type the access PUK code 00000 9999 00000 (default PUK)
4. Click “OK”
Web Server’s Home page appears.
IP
2
1
4
3

## Slide 31
5. Click “System configuration”
System configuration page appears
Configuration sequence:
Gateways and Devices configuration
Loads, groups and panel boards configurations
Bill of Consumptions configuration
5

## Slide 32
7.12.1 Gateways and Devices configuration
1. Click “Gateways and devices”
Gateway’s settings page appears
The page is divided into two sections:
section is the “Gateways” area.
section shows the “Gateway Settings” area, where the configuration fields for the selected gateway are available.
B
A
A
B
1

## Slide 33
2
5
1
4
3
7.12.1.1 Creating and Saving new Gateways
1. Click “Add”
2. Assign the gateway parameters: IP Address (required parameter) Name (required parameter) Description/Location (optional parameter)
3. Click “Save”
4. Click “Test” to verify the correct operation of the communication between the Web Server and the Gateway
5. Click “Devices” to configure the physical or virtual devices connected to the Gateway
Device’s settings page appears
The page is divided into two sections:
section is the “Added Devices” area.
section shows the “Device Settings” area, where the configuration fields for the selected device are available.
A
B
A
B

## Slide 34
Description of the Gateway selection button
IP address assigned to the gateway
Name of the gateway
Gateway status
  On
  Off
  Communication error
7.15.1.2 Creating and Saving of “Physical” Devices
- Procedure for Measure device with RS485 output
1. Click “Add”
2. Choose the Device family from the families list (e.g. Nemo D4-Le)
3. Choose the Model from the models list (e.g. MFD4421)
4. Assign the Device parameters: Modbus address (required parameter) Name (required parameter) Load type (optional parameter)
5. Click “Save”
6. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
Repeat the operations 1. to 6. to add more devices
3
2
1
4
1
6
5
3
2

## Slide 35
- Procedure for NEMO SX modules
1. Click “Add”
2. Choose the Device family from the families list
3. Choose the model from the model list
4. Assign the Device parameters: Modbus address of the Device/Group of devices NEMO SX (required parameter) Note: in case of a NEMO SX system in “remote addressing mode”, the Modbus address is composed as shown: “address of the device/group of devices” - “address of the NEMO SX interface to which the devices are connected” (e.g.: device address: 2, interface address: 1 → write: 2-1) Name (required parameter) Load type (optional parameter) Supply: current direction in the measuring sensors (required parameter for cat. Nos. SXMM63/MT63/MMT5)
5. Click “Save”
6. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
Repeat the operations 1. to 6. to add more devices
Note: pulse concentrator module NEMO SX (cat. no SXMIMP) is to be managed as a standard pulse concentrator (see next page).
Details for Measurement modules NEMO SX Supply: to ensure correct measurement of various electrical quantities, it is necessary to indicate the current versus trough the CT(s) or Rogowski sensor(s):
current versus upstream of tore/CT → choose Upstream (default setting)
current versus downstream of tore/CT → choose Downstream
1
4
6
5
3
2

## Slide 36
- Procedure for Measure devices with pulse output (Electricity, Water and Gas counters)
1. Click “Add”
2. Choose the Device family from the families list (e.g. Conto D1)
3. Choose the model from the models list (e.g. CE11165A2)
4. Assign the Device parameters: Modbus address (address of the pulse concentrator) - Position (required parameters) Name (required parameter) Load type (optional parameter) Note: for Water and Gas Counters, load type is automatically assigned
5. Choose the Concentrator from the list (e.g. IF4C001)
6. Click “Save”
7. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
Repeat the operations 1. to 7. to add more devices
Details for Pulse output Meters (Electricity, Water and Gas counters)
Position: is the input of the Concentrator (Cat. Nos IF4C001 or SXMIMP*) or of the Energy counter with pulse input counter function (Cat.Nos CE2DF3DTCL1, CE4DF3DTCL1 or CE4TBDTCL1) on which the pulse output of the counter is connected.
(* NEMO SX Device)
1
4
3
2
5
7
6

## Slide 37
- Procedure for “Generic” Measurement/Counting Devices with Modbus RS485 output
1. Click “Add”
2. Choose the Family “Other devices“ from the families list
3. Choose the model “Generic Modbus meter“ from the models list
4. Assign the Device parameters: Modbus address of the Measurement / Counting device (required parameter). Name (required parameter) Load type (optional parameter) Register (hex) - Word: in these 4 fields you must enter the following parameters: - Modbus register read code (3 or 4) - Modbus register of positive active energy (value in hexadecimal) - number of words to read - multiplying factor to use to obtain the correct value Note: these four information can be found in the documentation of the meter / counter, provided by the device manufacturer.
5. Click “Save”
6. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
Repeat the operations 1. to 6. to add more “Generic” measurement/counting devices
1
4
3
2
6
5

## Slide 38
- Procedure for Power factor controller ALPTEC
1. Click “Add”
2. Choose the Device family “ALPTEC” from the families list
3. Choose the Model from the models list
4. Assign the Device parameters: Modbus address (required parameter) Name (required parameter)
5. Click “Save”
6. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
Repeat the operations 1. to 6. to add more Power factor controllers
1
4
3
2
6
5

## Slide 39
7.12.1.3 Advanced options
In the “Devices” page
1. Select a Device
2. Click “Advanced”
3. In this page for each device configured by the user, it is possible to set following options: - “Exclude from totals”. Select this option if you don’t want that the quantities measured by this device are added on the histograms in the “Grand Total“ and “Partials” page of the menu “Consumptions”. Histograms of consumptions will be displayed only in the “Details” page of the menu “Consumptions”. (see details on page 39)
“Exclude alerts”. Option available for NEMO SX and ALPTEC devices. Allows you to disable/exclude reports of alert(s) on events related to these types of devices. Note: configuration of the type of events that cause a report, is available in the “Alert settings” page of the “Email and notification” menu of the Web server (see § 8.5.4)
- Customize the description of inputs and outputs for Multifunction State (SXMC02) and Multifunction Control (SXM0C1) Modules, of the NEMO SX range, in generic configuration.
4. Click “Save” to confirm settings
1
2
4
3

## Slide 40
Procedure to activate the “EQ device” function
EQ device is an optional function used to perform the energy quality check according to standard EN 50160. To do this is necessary set a device as “EQ device” in Gateways and devices page.
1. Select a Gateway
2. In correspondence of EQ device choose from the list box the device to set as energy quality device (in the list box are displayed only devices with THD or THD + Harmonics functions added to the selected gateway).
3. Click “Save”
Note: for each gateway is possible to set only one device as “EQ device”.
Software perform automatically the weekly check and shows the result in the Consumption Details page with the label “LAST WEEK EN50160 CHECK: OK or KO”
At the same time the software creates the folder “eqcheck ” in the web server’s data base saved on the HDD of the Web Server (see 8.4.3).
1
2
3

## Slide 41
Details for the option “Exclude from totals“
This option must be enabled if the measurement of a device is cumulative with the measurement carried out by a general measuring device.
In the example: consumptions of the line "Lighting” would be counted twice in the histograms of global consumption. The device 2 will be excluded from the totals to ensure the accuracy of the measurements, but its data will be displayed on the page "Details“ of the menu “Consumption”.
Description of the device selection button
Modbus Address (Modbus Address - Position for the counters with pulse output)
Name of the device
This symbol appears only if the device is a protection device and shows the circuit-breaker state:
  Open
  Closed
  Tripped
Device status
  On
  Off
  Communication error
Device 1 - General measure
Device 2 - Lighting
Excluded device
1
2
3
4

## Slide 42
7.12.1.4 System functions
ON/OFF Button
Allows to enable/disable a Gateway or a Device; the function is available only for Gateways and Devices.
1. Click “ON” to switch off a Gateway / Device
The selected Gateway / Device and the button switch into the OFF state.
Note:
The deactivation of a Gateway causes the deactivation of all devices connected to it.
If a device is turned-off, its measurement data will not be displayed in the "Devices“ page.
To return a Gateway / Device in the ON state, simply click "OFF“
1

## Slide 43
Button
Allows to erase a Gateway or a Device.
1. Click “Delete” in the “Gateway settings” or “Device settings” page
A confirmation page appears.
2. Click “Erase” to confirm the deletion of the Gateway or the Device
Note1: To erase a Gateway, is necessary delete all the devices connected to it at first!
LIST OF REQUIRED PARAMETERS:
Highly required parameters - Address/Position:
Modbus Address, a different Modbus address for each device connected to the same bus RS485
Positions, different for wiring reasons; (only for Counters with pulse output)
Essential parameter – Name:
Impossible to use several times the same name
If forgotten during the settings, Web Server will assign a default value (IP Address for Gateway, Modbus Address for Devices RS485, Modbus Address-Position for Devices with pulse output).
Parameter “Model”:
Possibility to have one, two or several identical models.
If forgotten during the settings is shown the message “Configuration Error”.
1
2

## Slide 44
7.12.2 Loads, Groups and Panel boards configuration
Optional setup, used to give a description of the electrical installation by panel board(s), load(s) and group(s)
1. Click “Loads, groups and panel boards”
Loads, groups and panel boards settings page appears.
2. Click “Panel boards”, “Loads” or “Measure Groups” to create a panel board, a load or a measure group.
Every page is divided into two sections:
- left section is the “Added Panel boards / Loads / Measure groups” area.
- right section shows the “Panel boards / Loads / Measure groups” settings area, where the configuration fields are available.
2
1

## Slide 45
7.12.2.1 Panel boards
CREATING AND SAVING PANEL BOARD
For a physical distribution of the different panel boards of the installation.
Recommended architecture: only one Gateway per Panel board
To create a Panel board:
1. Click “Add”
2. Assign the panel board parameters: Name (required parameter) Description/Location (optional parameter)
3. Click “Save”
Repeat the operations 1. to 3. to add more panel boards
ASSIGNMENT OF PANEL BOARDS
Return to the section “Gateways and Devices” in “System configuration”.
In the Gateway settings area of the Gateways page, is possible to assign each gateway previously created, to a Panel board.
Note: a gateway can be assigned to only one panel board.
1. Choose a Gateway
2. Choose a Panel board from the Panel boards list
3. Click “Save”
2
3
1
1
3
2

## Slide 46
7.12.2.2 Loads
CREATING AND SAVING LOADS
are available:
6 “pre-defined” categories (heating, air conditioning, etc.)
Category “Others” to display the measurement without Load assigned
8 additional categories, user-creatable
To create a Load:
1. Click “Add”
2. Assign the load parameter: Name (required parameter)
3. Click “Save”
Repeat the operations 1. to 3. to add more loads
Note: it is possible to have a maximum of 14 loads.
ASSIGNMENT OF LOADS
Return to the section “Gateways and Devices” in “System configuration”.
In the Device settings area of the Devices page, is possible to assign a Load to each virtual or physical Device previously created.
1. Click “Settings”
2. Choose a Device
3. Choose a Load from the Loads list
4. Click “Save”
2
3
1
2
3
4
1

## Slide 47
7.12.2.3 Measure groups
CREATING AND SAVING MEASURE GROUPS
For a logical distribution of the measuring points of the installation
To create a Measure group:
1. Click “Add”
2. Assign the measure groups parameters: Name (required parameter) Description/Location (optional parameter)
3. Click “Save”
Repeat the operations 1. to 3. to add more groups
ASSIGNMENT OF MEASURE GROUPS
Return to the section “Gateways and Devices” in “System configuration”.
In the Device settings area of the Devices page, is possible to assign a Measure group to each virtual or physical Device previously created.
1. Click “Groups”
2. Choose a Device
3. Choose a Measure group from the Measure groups list
4. Click “Save”
Repeat the operations 2. to 4. to assign a device to another group
Note: a device can be associated with several groups simultaneously (up to 5).
2
3
1
2
3
1
4

## Slide 48
7.12.2.4 System functions
DELETE Button
Allows to disable / erase a Panel board, a Load or a Measure group.
Note: For the “pre-defined” loads the disabling is the only function permitted.
In the Panel boards / Loads / Measure groups settings area:
1. Choose a Panel board / Load / Measure group
2. Click “Delete
An intermediate page in which, the deactivation (Disable) or the erasing (Erase) of the selected Panel board / Load / Measure group is proposed.
3. Click “Disable” to deactivate the Panel board / Load / Measure group or “Erase” to remove definitively the Panel board / Load (possible only for the “user-creatable” loads) / Measure group.
1
2
3

## Slide 49
  By clicking on “Disable” the selected Panel board / Load / Measure group, goes into “Deactivated” state.
  This state is indicated by the symbol near to the Panel board / Load / Measure group’s name.
To enable a Panel board / Load / Measure group, simply click “Enable“.

## Slide 50
7.12.3 Bill of Consumptions configuration
This optional setting, based on Cost Rules, allows the economic accounting of Electricity, Water and Gas consumptions
1. Click “Bill of consumptions”
Bill of Consumptions setting page appears
The page is divided into three sections:
section shows the Cost Rules created by the users.
Note: in a new factory web server or in an updated web server where no tariffs was configured, this area is empty. If, on the other hand, Electricity, Gas or Water tariffs were already configured before the updating of an installed web server, they are here displayed in a Rule with the wording ”DEFAULT”
section is the area where is possible to assign:
Currency using the three-letter alphabetical code according to ISO 4217 standard (e.g. EUR, USD, GBP, …)
Conversion factor (kWh/m3) to display Gas consumptions also in “Equivalent kWh”. This parameter appears only when Gas page is selected
Note: Conversion factor should be provided by your Gas supplier; contact it to get the conversion rate
section shows configuration parameters for the selected/new Cost Rule
1
B
C
A
A
C
B

## Slide 51
7.12.3.1 Creating and Saving Tariffs and new Cost Rules
1. Select Electricity, Gas or Water
2. Click “Add”
Section with configuration parameters appears
3. Clicking on ”Edit” button, the page where it is possible to create Tariffs to be assigned to Cost Rules is displayed.
For each type of load (Electricity, Gas, Water) it is possible to create up to 5 tariffs with a different display colour and up to 5 different cost values can be assigned for each tariff, specifying the validity date.
2
1
3

## Slide 52
Procedure to create Tariffs
Each Tariff is defined by assigning the following parameters (some are mandatory while others are optional):
- the Name - the Colour by which the tariff will be identified in histograms and charts - one or more Prices - validity Date for each price
- To create a Tariff
In the Tariffs edit page:
1. Select a Tariff button
Assign Tariff parameters: 2. the Name 3. the Colour 4. Price per kWh of Electricity or per m3 of Gas/Water 5. the Date from which the set price is valid Note: if only one price is assigned to a tariff it is not necessary to set a validity date. If not, a validity date must be associated to each price entered; Web server automatically will assign correct price to tariff according the date set in this page.
6. Click “Save”
Repeat the operations 1. to 6. to add more tariffs
7. Click “Cost Rules” to return to the previous page
4
1
2
7
5
3
6

## Slide 53
Procedure to create Cost Rules
Each cost rule is defined by assigning the following parameters (some are mandatory while others are optional): - a Tariff among those previously created - a specific validity date or validity period - a time frame where the rule is true - a checkbox useful to define rules that are repeated every year on the same day or period (e.g. Christmas, New Year's Day, etc...) and which constitute an exception in standard programming - several checkboxes to define for which days of the week the rule is true (is possible to check one or more specific days or “every days”)
- To create a Cost rule
In the Cost Rules page:
1. Select one of the Tariff previously created
2. Define: - a specific validity date or period (If necessary) - a time frame where the rule is true Note: flagging “repeat every year” checkbox, you can define that the rule being created is valid every year for the date or period indicated
3. Select the days of the week when the rule is valid
4. Click “Save”
Repeat the operations 1. to 4. to add more rules
Notes: - active rule is highlighted by the symbol flashing to the left of the name of the associated tariff
- it is always possible to add or edit a Tariff by selecting any of the rules created and pressing the “Edit” button
1
2
3
4

## Slide 54
Example 1: Rule with Tariff 1, valid all year round from 00:00 to 18:59, from Monday to Friday
Example 2: Rule with Tariff 2, valid all year round from 19:00 to 23:59, from Monday to Friday
Example 3: Exception for Christmas day with Tariff 2, valid every year, all day whatever the day of the week

## Slide 55
Example 4: Exception for the month of March 2020; the rule created provides Tariff 3 all day any day of the week
IMPORTANT: the operating logic of the cost rules is based on a “true” or “false” criteria of the rules. The web server analyzes the rules created by the user starting from the top down. Once a true rule has been identified, the server stops the analysis until the end of the period defined in the true rule. For this reason it is necessary to arrange the created rules and move them using the “Move up” and “Move down” buttons placing the Exceptions always in the first positions in the rules list.
Using Rules of the example 4, correct order is (see image below): 1st: Rule related to March 2020 with Tariff 3 2nd: Rule related to Christmas day with Tariff 2
3rd: Rule from 00:00 to 18:59 with Tariff 1
4th: Rule from 19:00 to 23:59 with Tariff 2

## Slide 56
Consumptions costs set and assigned with previous versions
As previously said, updating a web server in which Electricity, Gas or Water consumption costs were already set (see image below as example), in the new “Bill of consumptions” page these are displayed as an always valid Rule (one for each load type) with which the tariff called “DEFUALT” is associated.
Bill of consumptions page up to 3.7.1 version, with consumption costs set
Bill of consumptions page from 3.8.1 version, with Rule associated to “Default” tariff
If you don’t want to create new Tariffs or Cost Rules, you can keep this configuration with which web server continue the economic accounting of Electricity, Water and Gas consumptions as before. Otherwise, before creating new Tariffs and Rules, we suggest to you to edit “Default” Rule fixing an end validity date (e.g. the end of the month preceding the month in which the web server was updated)

## Slide 57
7.12.4 Configuration of the data sample rate
Optional setting, allows to edit the recording time of Electricity data including statistical data (if available in the devices), of Water and of Gas in the Web Server database.. Note: default value: 15 minutes
Parameter “Sample rate” affects :
- histograms updating in the consumptions display pages
- Recording of consumptions data in the database
- recording of the statistical values (average values, minimum, maximum, ...) for measuring devices which have these values
- “CSV” files saved in the FTP space of the web server
- “CSV” files downloaded with the “Data download” function
Procedure to edit the setting:
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Web server settings”
1
2

## Slide 58
3. Click “CSV and other settings”
4. Select the “Sample rate” value.
5. Click “Save”.
Note: Editing of this setting does not affect data already saved by the Web Server before changing the value.
4
5
3

## Slide 59
7.12.5 Master/Slave function
This function allows you to use a web server as “Master” of one or more “Slave” web servers in order to let the “Master” acquire consumption data recorded by the “Slaves”.
The function allows you to manage, for example: - installations with multiple levels - systems with more than 255 measuring points
Example 1:
Example 2:
The data that can be acquired from the “Master” web server are the following: - Positive active Energy of a specific Device
- Positive active energy of a specific Load
- Positive active energy of a specific Measure group
- Total Positive active energy of all Electrical Loads
Web Server Master
LEVEL 1
LEVEL 2
Site A
Web Server Slave 1
Site B
Site C
Web Server Slave 3
Web Server Slave 2
Web Server*
LEVEL 3
Area A
Web Server Master
LEVEL 1
LEVEL 2
Site A
Web Server Slave 1
Site B
Area B
Serveur
Web
Web Server Slave 2
* Web server simultaneously Master and Slave

## Slide 60
7.12.5.1 Activation of the Function
This configuration is to be performed only on Slave Web Server(s) and is used to give the Master permission to access the data registered by the Slave(s).
Procedure to activate the function on the Slave Web Server(s): In the Web Server’s Home page
1. Click “Web Server configuration”
2. Click “Web server settings”
3. Click “Modbus settings”
3
1
2

## Slide 61
4. Click to Enable (“ON”) the Modbus TCP Server used for Master/Slave function
5. Click “Save” 2 times to confirm
Note: System will restart automatically when settings are saved
7.12.5.2 Creating and Saving of “Virtual” Gateways and Devices
Procedure for creating and saving “Virtual” Gateways and Devices is the same used for physical Gateways and Devices.
In the Web Server’s Home page
1. Click “System configuration”
2. Click “Gateways and devices”
2
1
4
5

## Slide 62
1. Click “Add”
2. Assign the parameters to the Virtual gateway = Slave Web server: IP Address of the Slave Web Server (required parameter) Name (required parameter) Description/Location (optional parameter)
3. Click “Save”
4. Click “Test” to verify the correct operation of the communication between the Web Server and the Gateway
5. Click “Devices” to configure the devices connected to the Slave Web server
Device’s settings page appears
1. Click “Add”
2. Choose the family “WSMEASURE” from the families list
3. Choose the Model from the models list
4. Assign the Device parameters: Name (required parameter) Load type (optional parameter) Note: Modbus Address is automatically filled
5. Enter the specific “Remote ID” of a Device, Load or Measure Group configured in the Slave Web server or 6. Click on “All” to return Total Active Energy of all Electrical Loads of the slave web server (the “Remote ID” field will be filled automatically)
7. Click “Save”
8. Click “Test” to verify the correct operation of the communication between the Device and the Gateway
1
2
5
4
3
4
5
2
3
7
8
6
1

## Slide 63
Details for the “Remote ID” parameter
The “Remote ID” is the ID number of a Device, Load or Measure Group in the slave web server database.
This unique number is assigned to a Device, Load or Measure Group during the system configuration and it is shown:
- in the “Gateway and devices” page for Devices (see image below)
- in the “Load types” page for preconfigured or user-created Loads (see image below)
- in the “Measure groups” page for Measure Groups (see image below)

## Slide 64
Description of the device selection button
Modbus Address (fixed value equal to 247) - Indication of the virtual device type: 247 - 1XXXX = Positive active energy of the Device with ID = XXXX 247 - 2YYYY = Positive active energy of the Load with ID = YYYY 247 - 3ZZZZ = Positive active energy of the Measure Group with ID = ZZZZ 247 - 29999 = Total Positive active energy of all Electrical Loads
Name of the device
Device status
  On
  Off
  Communication error
2
1
3

## Slide 65
8. Use
8.1 Access
The access to the Web Server data is protected by identification codes (PIN and PUK codes).
Four types of “default” users are configurated:
“administrator”
“greenUp”
“installer”
“user”
The home page ("home") will be different depending on the type of user that access to the device.
8.1.1 Access right
“administrator”
Access to the pages:
Web Server configuration
System configuration
My panel board (display of all measuring/metering devices)
Consumption: data & diagrm.
Reports & Data download
Reports: alarms
Default access PIN code:
99999 (5 characters)
Default access PUK code:
00000 9999 00000 (14 characters)
“installer”
Access to the pages:
System configuration
My panel board (display of all measuring/metering devices)
Consumption: data & diagrm.
Reports: alarms
Default access PIN code:
55555 (5 characters)
Default access PUK code:
00000 5555 00000 (14 characters)
“user”
Limited access to display pages of data (not configurations possible in mode “user”):
Consumption: data & diagrm.
Reports: alarms
Default access PIN code:
11111 (5 characters)
Default access PUK code:
00000 1111 00000 (14 characters)

## Slide 66
8.1.2 Creating a new User
Only the user “administrator” can add new users.
1. Click “Web Server configuration”
Web Server configuration’s page appears
2. Click “Users”
1
2

## Slide 67
Users configuration page appears
3. Click “Add”.
4. Assign a name to the new user.
5.- 6. Type the PIN and PUK codes for the new user.
7. Choose which pages the new user can see.
8. Click “Save”
8.1.3 Changing of the access rights
The access rights of a user can be modified only by the user “administrator”
In the Users configuration page
1. Choose from the list a “name of a user” (ex. installer) to edit it.
2.- 3. Type the PIN and PUK codes for the user to edit.
4. This option allow to disable a user without erase it once the “Save” button is clicked.
5. Choose, for the user to edit, which pages it can see.
6. Click “Save”.
5
1
6
4
2
3
4
3
5
6
7

## Slide 68
8.1.4 Logout procedure
The symbol appears on all pages of the web server.
1. Click “logout”
A confirmation page appears.
2. Click “Logout” or “Lock” to confirm the exit from the web server.
Note:
Logout  closing the session, reconnection with the PIN code
Lock  temporary disabling of the application, reconnection with the codes PIN+PUK
1
2

## Slide 69
8.2 Data display pages
8.2.1 My panel board
In the Home Page
1. Click “My panel board”
Devices page appears
The page is divided into three sections:
section shows the devices added by the users with their characteristics and status icons. It is possible to choose a device per Gateway , Panel board or "All Devices“
section is the area where is possible to select two pages:
Measure: display of the quantities measured by a device:
  Electricity measuring devices: Energy, Power, Voltages / Currents / Frequency, THD (if available on the Device) and Harmonics (if available on the Device) Note: for “generic” measurement/counting devices and “Virtual” devices created with the Master/Slave function, only the table with the value of positive active energy is available.
  Water Counters: Water consumptions
  Gas Counters: Gas consumptions
State/Com.: page dedicate to NEMO SX devices; display of devices status, control buttons… for each NEMO SX device/group of devices
section shows the values measured by the selected device, status icons and command buttons (if available).
C
B
A
A
C
B
1

## Slide 70
For Power Factor Controllers of ALPTEC range, “My panel board” page is structured as follows:
In the Home Page
1. Click “My panel board”
Devices page appears
The page is divided into three sections:
section shows the devices added by the users with their characteristics and status icons. It is possible to choose a device per Gateway , Panel board or "All Devices“
section is the area where is possible to select two pages:
Measure: display of parameters and electrical quantities measured by the Power Factor Controller:
  Steps: State ( : Step not inserted, : Step inserted), Residual power (in % for APLTEC3.2/5.2/8.2 and in kvar for ALPTEC8), Number of insertions and Insertion time for each step; indication of the Global state of Steps (OK or Default), AUTO/MAN control button used to show the state of the power factor controller and to switch the device between two operating modes
  Others quantities: Power, Power Factor, Voltages/Currents/Temperature, THD and Harmonics
State/Com.: display of residual time to maintenance (for APLTEC3.2/5.2/8.2) and possibility to reset this time
section shows the values measured by the selected power factor controller
B
A
C
A
C
B
1

## Slide 71
Description of the device selection button
Modbus Address (Modbus Address - Position for counters with pulse output or Modbus Address - Indication of the virtual device type for the Master/Slave function)
Name of the device
Symbols of the functions associated to the Device
  Measure
  State
  Command
  Link Functionality
This symbol appears only if the Device integrates the state function related to a protection device and shows the circuit-breaker state:
  Open
  Closed
  Tripped
Device status
  On
  Off
  Communication error
2
1
4
5
3

## Slide 72
8.2.2 Consumptions: data & diagrm.
In the Home Page
1. Click “Consumptions: data & diagrm.”
Consumptions page appears
Are available 5 ways of displaying data:
Grand Total (Consumption of the entire installation)
Partials (Consumptions per Load and/or Measure group)
Compare (Comparison of the Global Consumptions between two Devices)
Details (Consumptions of a single Device)
Tariffs (Display of the Cost of Consumptions according to configured Tariffs)
1

## Slide 73
For each page are available:
Histograms of Consumptions divided per:
Day (per hour)
Month (per day)
Year (per month)
Comparison between the actual and the previous value (ex. today/yesterday, etc.)
Values in:
Wh (and multiples of Wh), dm3 (and multiples of dm3) of water, dm3 (and multiples of dm3) of gas and "Wh (and multiples of Wh) equivalent" of gas. Note: displayed values (resolution , decimal values, etc.) depend only on the quantities read by the measuring instruments.
EUR (or other configured currency)

## Slide 74
8.2.2.1 Grand Total
1. Click “Grand total”
Grand total page appears
Visualization of Total Energy Consumptions (Ea +) on histograms divided per Load
2. Click “Day”, “Month” or “Year” to view the consumptions on a different time period (Day (hours) / Month (days) / Year (months))
3. Click “Overall” to display the page of the Overall Consumptions (Electricity, Gas and Water) of the system.
Note: in this visualization, consumption data for “virtual” devices not excluded from Total are also taken into account.
3
2
1

## Slide 75
Overall consumptions page appears
Visualization of the Overall Consumptions of the system on tables and on a pie chart showing:
consumptions subdivided per type: Electricity (blue area) Gas (violet area) Water (yellow area)
consumptions valued according to the measurement unit and the configured currency
4. Click “Day”, “Month” or “Year” to view the consumptions on a different time period (Day (hours) / Month (days) / Year (months))
Note: in this visualization, consumption data for “virtual” devices not excluded from Total are also taken into account.
4

## Slide 76
8.2.2.2 Partials - Groups and load type
1. Click “Partials - Groups and loads”
Visualization of Partials Consumptions on histograms per Day / Month / Year
    2. Click to view the consumption of a specific Measure group or of “all groups”
    3. Click to view the consumption of a specific Load (ex. Ventilation, Water, Gas, …) or of “All electricity loads”
    Note: in this visualization, consumption data of “virtual” devices according to the Loads and/or the assigned Measure Groups are also taken into account.
2
3
1

## Slide 77
8.2.2.3 Compare
1. Click “Compare”
  Comparison of the Consumptions between two Devices.
    2. Click to select the two “physical” or “virtual” Devices to compare
    Note: Selecting two non homogeneous Devices (ex Electricity and Gas), comparison is evaluated only according to the currency (EUR or other currency) and not according to the measurement units. It is not possible to compare kWh of energy and “Equivalent kWh of gas.
    3. Click “Total” or “Details” to view the Total or Detailed comparison between the two selected Devices
4. Click “Day”, “Month” or “Year” to view the consumptions on a different time period (Day (hours) / Month (days) / Year (months))
4
2
3
1

## Slide 78
A
B
C
8.2.2.4 Details
1. Click “Details”
The page is divided into three sections:
section shows the devices added by the users with their characteristics and status icons. It is possible to choose a device per Groups / Loads or "All Devices“
section is the area where is possible to select two pages:
Measure: display of the quantities measured by a device:
  Electricity measuring device: Energy, Power, Voltages / Currents / Frequency, THD (if available on the Device) and Harmonics (if available on the Device) Note: for “generic” measurement/counting devices and “Virtual” devices created with the Master/Slave function, only Energy histograms are available.
  Water Counters: Water consumptions
  Gas Counters: Gas consumptions
State/Com.: page dedicate to NEMO SX devices; display of devices status… for each NEMO SX device/group of devices
section shows the histograms of the consumptions, values measured by the selected device and status icons (if available).
A
C
B
1

## Slide 79
For Power Factor Controllers of ALPTEC range, “Details” page of the “Consumptions: data & diagrm.” menu is structured as follows:
1. Click “Details”
Details page appears
The page is divided into three sections:
section shows the devices added by the users with their characteristics and status icons. It is possible to choose a device per Gateway , Panel board or "All Devices“
section is the area where is possible to select two pages:
Measure: display of parameters and electrical quantities measured by the Power Factor Controller:
  PF: linear graphs with power factor trend
  Others quantities: Power, Power Factor, Voltages/Currents/Temperature, THD and Harmonics
section shows the values measured by the selected power factor controller
1
B
A
C
A
C
B

## Slide 80
8.2.2.5 Tariffs
1. Click “Tariffs”
Tariffs page appears
Are available 2 ways of displaying data:
Total (Consumption costs of the entire installation)
Details (Consumptions costs of a single Device)
1

## Slide 81
8.2.2.5.1 Total
1. Click “Total”
Visualization of Total cost of Consumptions in EUR (or other configured currency) on a pie chart showing costs subdivided according to the configured tariffs (in the example 4 tariffs configured and only 3 with data)
2. Clicking on the drop-down menu it is possible to select or deselect the tariffs to be displayed on the pie chart (the pie chart is automatically updated)
3. Click “Electricity”, “Gas” or “Water” to view the costs of this type of load
Note: in this visualization, consumption data for “virtual” devices not excluded from Total are also taken into account.
1
3
2

## Slide 82
8.2.2.5.2 Details
1. Click “Details”
The page is divided into two sections:
section shows the devices added by the users with their characteristics and status icons. It is possible to choose a device per Groups / Loads or "All Devices“
section shows the histograms with the Cost of Consumptions in EUR (or other configured currency) subdivided according to the configured tariffs
Clicking on the drop-down menu it is possible to select or deselect the tariffs to be displayed on the histograms (histograms are automatically updated).
1
A
B
A
B

## Slide 83
8.2.2.6 Advanced histograms and charts display
For histograms and pie charts of the menus “Partial – Groups and Load type”, “Details”, ”Tariffs-Total” and ”Tariffs-Details” an advanced display mode is available.
- Full screen display
1. Clicking on the button , histograms/charts can be enlarged to full screen. This function can be useful for projecting histograms/charts on screens in public places, processing departments, ... to create an awareness on consumption.
Note: image format and resolution will depend on the screen on which the data will be displayed (see example below for a screen 16:9)
2. To return to the standard format, press the button at the top right.
2
1

## Slide 84
- Detailed view and direct download of data
1. Clicking on the button , it is possible to browse the histograms/charts in detailed mode by:
Day (per hours)
Month (per days)
Year (per months)
10 years (per years)
2. Click to select the histogram/chart viewing period (Day, Month, Year or 10 years)
3. Click to choose a specific date in the selected period
4. Clicking on two arrows ( or ) it is possible to pass from one to another histogram/chart in the selected period (e.g. today, yesterday, two days ago, ...)
5. Clicking on the button , it is possible to download a “.csv” file named “datalogger.csv” with the data saved by the web server in the selected period
6. Click to return to the standard view
Note: it is still possible to put in full screen this type of histogram by pressing the button .
1
2
3
5
4
6

## Slide 85
Description of the device selection button
Modbus Address (Modbus Address - Position for counters with pulse output or Modbus Address - Indication of the virtual device type for the Master/Slave function)
Name of the device
Symbols of the functions associated to the Device
  Measure
  State
  Command
  Link Functionality
This symbol appears only if the Device integrates the state function related to a protection device and shows the circuit-breaker state:
  Open
  Closed
  Tripped
Device status
  On
  Off
  Communication error
2
1
4
5
3

## Slide 86
8.2.3 Link Functionality
This function allows you to link two NEMO SX modules to create automatic actions between a module that generates an event and a module that performs an action as a result of the event; these automations, once programmed, can run independently without a connection to a manager is needed.
Programming is done using the NEMO SX configuration software. The Web Server can see which links are created between the NEMO SX modules.
In the Web Server’s home page
1. Click “System configuration”
System configuration page appears
2. Click “Link Functionality”
Link functionality page appears
1
2

## Slide 87
In this page are shown the existing links between the NEMO SX modules configured in the Web Server: - on the left, modules that generate events - on the right, modules that generate actions in response to the events
Each module is indicated with its name, function, name of the Gateway under which is the NEMO SX module and the Modbus address of the NEMO SX module
In case of an error an alert icon is displayed. Note: to check and correct errors it is necessary to use the NEMO SX configuration software.
At the same time, the symbol appears in the device selection button to indicate that there is one or more modules that have been configured as part of a Link

## Slide 88
8.3 Historical of consumptions
All the measured quantities are saved automatically in files “.CSV” compatibles with Excel or “csv” reader. It could be necessary to export these files to manipulate the information; to do this are required some settings in the Web server.
8.3.1 CSV files options
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Web server settings”
3. Click “CSV and other settings”
1
3
2

## Slide 89
1
2
4
6
7
5
4.Click to set the CSV decimal separator: “point” or “comma” (default)
5. Click to set the CSV fields separator: “comma” or “semicolon” (default)
6. It’s possible to change the default password (default password: wsmeasure) used to access to the CSV files contained in the HDD of the Web Server. (See § 8.3.2)
7. Click “Save”
Note: The system restart automatically when settings are saved.
8.3.2 Access to CSV files
Access to CSV files contained in the HDD of the Web Server, it is possible via File Transfer Protocol (FTP):
ACCESS VIA FTP
Type the command FTP://”Web Server IP Address” (ex. FTP:// 172.168.1.101) in the Web browser or in the “address area” of a folder; an intermediate page appears.
User name and password are requested:
1. Type the requested fields
User name: type “wsmeasure” (default user name; not changeable by the user).
Password: type “wsmeasure” (default password) or “password modified by the user” (see § 8.3.1)
2. Click “Log On”

## Slide 90
Access to the server by web browser allows you to view and/or saving single “CSV” files only.
For the full download of all “CSV” files at once, access to the web server via the “address area” of a folder.

## Slide 91
8.3.3 Management of CSV files
CSV files are created automatically according to the settings done by the user in “System Configuration”.
Files are saved in the HDD of the Web Server in the following sub-folders:
“devices”: contains the data recorded by each device (multifunction device, energy meter, etc.)
“energy”: contains data related to energy consumption Ea+ (files are recorded per “all devices” / “Loads” / “Groups”)
“eqcheck”: contains information on the energy quality (according to EN 50160) read by a device set as “Eq device” in Gateways and Devices (see page 36)
“gas”: contains data related to gas consumption (files are recorded per “Devices” and “Groups”)
“overall Total”: contains data related to total consumptions of electricity, gas and water
“settings”: contains files which show the system structure detailed per IP and Modbus addresses, groups, loads, etc.
water: contains data related to water consumption (files are recorded per “Devices” and “Groups”)
Notes:
- all consumption values are saved in Wh for Electricity data and dm3 for Water and Gas data
- saved values (resolution, decimal digits, etc.) depend only on the quantities read by the measuring instruments.

## Slide 92
8.3.3.1 “devices” folder
It contains a folder for each device set in the system.
Folder name: “Device ID”
Each device folder contains a series of “.csv” files named “ID_type of data recorded_sampling period”
ID: (identification number of the “physical” or “virtual” device in the database) is an unique number assigned to the device during the system configuration and it is shown in the Gateway and devices page (see image below)
type of data recorded: energy, gas, water, statistics, THD, harmonics, etc.
sampling-period: year-month of recording

## Slide 93
8.3.3.2 ”energy” folder
It contains a series of “.csv” files with the recording of energy consumptions subdivided per “Devices”, “Groups” and “Loads”. Files name “type_sampling period_file version”
type: consumptions distributed per devices, groups or loads
sampling period: year-month of recording
file version: increases in case of changes in the system configuration (adding of a Load/Group/etc.)
8.3.3.3 ”eqcheck” folder
It contains a file named
“eqcheck_sampling period_file version”
sampling period: year of recording
file version: increases in case of changes in the system configuration (changing of EQ device)
8.3.3.4 ”gas” folder
It contains a series of “.csv” files with the recording of gas consumptions subdivided per “Devices” and “Groups” Files name “type_sampling period_file version”
type: consumptions distributed per devices or groups
sampling period: year-month of recording
version: increases in case of changes in the system configuration (adding of a Group/etc.)
8.3.3.5 ”overall total” folder
It contains a series of “.csv” files with the recording of total consumptions of energy, gas and water
Files name “type_sampling period”
type: consumptions distributed per cost (currency set) or per values (kWh of energy, m3 of gas and m3 of water)
sampling period: year-month of recording

## Slide 94
8.3.3.6 ”settings” folder
It contains two files which show the system structure detailed per Gateways IP, Modbus addresses, groups, loads, etc.
8.3.3.7 ”water” folder
It contains a series of “.csv” files with the recording of consumptions subdivided per “Devices” and “Groups” Files name “type_sampling period_file version”
type: consumptions distributed per devices or groups
sampling period: year-month of recording
version: increases in case of changes in the system configuration (adding of a Group / etc)

## Slide 95
8.4 Reports & data download
8.4.1 Data Download
This function allows you to directly export consumption data in “.csv” format for a single device, a group of devices or for all devices installed in the system.
In the Web Server’s home page
1. Click “Reports & data download”
2. Click “Data download”
Data download settings page appears
2
1

## Slide 96
The page is divided into two sections:
section shows the “physical” or “virtual” devices added by the users with their characteristics and status icons. It is possible to create a list of Meter devices, Groups or Loads
section is the area where, once performed a selection, is possible to set:
starting and ending date of the reference period
whether to include in the download also costs file(s)
sample rate: 15 minutes (default), 1 hour or 1 day
To download csv files:
1. Click to select the list type that will be displayed: Meter Devices (default), Groups or Loads
2. Click to select Devices / Groups or Loads one by one (objects selected are highlighted in green) or 3. click “Select All” to select all Devices / Groups or Loads at once
4. Type starting and ending date
5. Click if you want to include in the download also a file with costs
6. Choose the sample rate according to which consumption and costs data will be grouped
7. Click “Download” to complete the process
An intermediate window with file(s) creation progress appears
A
B
A
B
1
2
4
5
3
6
7

## Slide 97
At the end of file creation process
8. Click “Download”
A pop-up window appears
9. Click to save the file on your computer , then 10. click “OK”
Files are now downloaded on your computer from the web server’s database in an archive named “reportdata.zip”.
Note: files will contain only data correctly saved on the database of the software; if a device is in communication error state or the web server is not running properly, consumption data won't be present on downloaded files.
8
9
10

## Slide 98
In the .zip archive you can find a file with consumption data and a file with costs data for each consumption type: electricity, gas and water for the selected Device(s) / Load(s) or Group(s)
To perform a new csv files download
11. Click “Cancel”
A pop-up window appears
12. Click “Yes” to return to the Data download settings page
12
11

## Slide 99
8.4.2 Reports
This function allows you to create a “.pdf” report starting from data contained in the database saved of the web server. Two types of reports are available:
a general report, monthly or yearly, containing overall consumption data of the system divided per type: Electricity, Gas and Water
a detailed report, monthly or yearly, containing consumption data of the selected Device(s).
In the Web Server’s home page
1. Click “Reports & data download”
2. Click “Reports”
Reports settings page appears
1
2

## Slide 100
The page is divided into two sections:
section shows the “physical” or “virtual” devices added by the users with their characteristics and status icons
section is the area where is possible to select:
which type of report: Summary or Detailed
the report period: Monthly or Yearly report
specific month and year
To create a Summary report:
To create this kind of report it is not necessary to select any device because this is a general document that contains Overall consumption data.
1. Select “Summary report”
2. Click to choose the report period: monthly or yearly
3. Choose month and year (for monthly reports) or only the year (for yearly reports)
4. Click “Download” to complete the process
A pop-up window appears
A
B
A
B
4
1
2
3

## Slide 101
5. Click to save the file on your computer , then 6. click “OK”
The file is now downloaded on your computer from the web server’s database.
Note: files will contain only data correctly saved on the database of the software; if a device is in communication error state or the web server is not is not running properly, consumption data won't be present on downloaded files.
In the destination folder you can find a file named:
“Report type and period”
report type: monthly or yearly report
period: year-month (for monthly reports) or year (for yearly reports)
To create a Detailed report:
1. Select “Detailed report”
2. Click to filter the Devices list per Groups / Loads or “All Devices“
3. Click to select Devices one by one (objects selected are highlighted in blue) or 4. click “Select All” to select all Devices at once
5. Click to choose the report period: monthly or yearly
6. Choose month and year (for monthly reports) or only the year (for yearly reports)
7. Click “Download” to complete the process
A pop-up window appears
5
6
6
2
3
4
5
7
1

## Slide 102
8. Click to save the file on your computer , then 9. click “OK”
The file is now downloaded on your computer from the web server’s database.
Note: files will contain only data correctly saved on the database of the software; if a device is in communication error state or the web server is not is not running properly, consumption data won't be present on downloaded files.
In the destination folder you can find a file named:
“Report type and period”
report type: monthly or yearly report
period: year-month (for monthly reports) or year (for yearly reports)
8
9

## Slide 103
8.5 Pushing e-mail and notifications
This function allows you to send via e-mail, monthly or yearly, to one or several e-mail address(es) an automatic reports in “.pdf” or in “.csv” format. To do this are required some settings in the Web server.
8.5.1 E-mail settings
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Email and notification”
3. Click “Email”
3
1
2

## Slide 104
Email configuration page appears
This page is used to configure the sender e-mail profile; e-mail recipients will receive messages containing alerts, events, reports, … with the email address configured here as “sender”.
1. Type the sender complete e-mail address (ex. abc@gmail.com)
2. Type the others e-mail account elements:
User: is the user name with which the sender access to his e-mail account
Password: is the password with which the sender access to his e-mail account
SMTP server name: is the Simple Mail Transfer Protocol name of the e-mail provider (ex. for gmail: smtp.gmail.com).
SMTP server port: optional setting used if the SMTP server port indicated by the provider is different from the default port value (port 465).
3. Enable SSL: Secure Sockets Layer is an encryption system that is used by all those organizations that need to transit safely and indecipherable data, so that only the intended recipient can view it. Enable this option if it’s indicated by your e-mail provider.
Note: the elements of points 2. and 3. are obtainable from your email provider or, for the main providers, by internet with a search engine looking for the SMTP characteristics for the outgoing mail.
4. Click “Save”
5. Clicking “Test” a sample e-mail is sent to the sender e-mail address set in this page in order to test the connection/configuration
1
2
3
5
4

## Slide 105
8.5.2 Telegram
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Email and notification”
3. Click “Telegram”
Telegram configuration page appears
Telegram is a cloud-based mobile and desktop messaging application with a focus on security and speed
3
1
2

## Slide 106
3
4
5
4
This page is used to configure the sender Telegram profile; Telegram users will receive messages containing alerts, events, … with the Telegram BOT configured here as “sender”.
Procedure:
1. Download the application (available for free for Android, iOS and Windows phones) on your smartphone and follow the installation process and the user profile configuration
2. Create the BOT Telegram using the procedure described on the application site (https://core.telegram.org/bots#3-how-do-i-create-a-bot). Note: BOT is a simply Telegram account used to create services.
3. Type the account elements :
- Name: name set in the BOT configuration process
Token: unique alphanumeric code created during the BOT configuration process; It is used to identify univocally the BOT
Password: it is created and inserted directly on this page; it is used to recognize users enabled to receive notifications from the Web server
Note: in this page will also appear the list of all users who have requested to receive notifications.
4. Click to enable/disable sending notifications to each Telegram user
5. Click “Save”
6. Clicking “Test” a sample massage is sent to all selected Telegram users in order to test the connection/configuration
Note: a telegram user, to be enabled to receive notifications from the Web server, will have to open the Telegram app on its smartphone and send to the BOT a message containing the password configured in this web page.

## Slide 107
8.5.3 Automatic reports
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Email and notification”
3. Click “Automatic reports”
Automatic report configuration page appears
3
1
2

## Slide 108
The page is divided into two sections:
section shows the “physical” or “virtual” devices added by the users with their characteristics and status icons
section is the area where is possible to select and set:
which type of report: Summary or Detailed
the report period: Monthly or Yearly report
the report format: pdf or csv
the e-mail address(es) of recipient(s). Note: to enter multiple email addresses, use the comma (,) as separator (ex. aaa@bbb.xy,ccc@ddd.wz)
To set the sending of a Summary report:
To create this kind of report it is not necessary to select any device because this is a general document that contains Overall consumption data.
1. Select “Summary report”
2. Click to choose the report period: monthly or yearly
3. Click to choose the report format: pdf or csv
4. Click to choose the report Delivery frequency: Monthly, Weekly or Daily
5. Type e-mail address(es) of recipient(s)
6. Click “Save” to complete the process
According to the selected period recipient(s) will receive the selected Summary report
A
B
5
6
1
2
3
4
A
B

## Slide 109
To set the sending of a Detailed report:
1. Select “Detailed report”
2. Click to filter the Devices list per Groups / Loads or “All Devices“
3. Click to select Devices one by one (objects selected are highlighted in blue) or 4. click “Select All” to select all Devices at once
5. Click to choose the report period: monthly or yearly
6. Click to choose the report format: pdf or csv
7. Click to choose the report Delivery frequency: Monthly, Weekly or Daily
8. Type e-mail address(es) of recipient(s)
9. Click “Save” to complete the process
According to the selected period recipient(s) will receive the selected Detailed report
1
5
2
3
8
9
4
6
7

## Slide 110
8.5.4 Alert settings
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Email and notification”
3. Click “Alert settings”
Alert settings page appears
3
1
2

## Slide 111
This page is used to set the type(s) of alarm/event for which are sent e-mail or Telegram messages
1. Select error/event causing the sending of e-mail or Telegram messages:
State change
Measure threshold
Configuration or installation error
Communication error
Power Factor Controller (ALPTEC)
2. Flag “Send email to” and type e-mail address(es) of recipient(s) and the object of the e-mail message if you want to send alert e-mail
3. Flag “Send Telegram” if you want to send alert Telegram messages
4. Click “Save”
1
2
3
3

## Slide 112
8.6 Reports: alarms
This function allows the automatic creation and display of the list of alarms, events, … , registered by each Modbus RS485/NEMO SX interface (cat.no SXI485) installed in the system.
In the Web Server’s home page
1. Click “Reports: alarms”
The page with the list of registered alarms appears
The page shows:
Data & Time of the alarm, event, …
Name assigned to the device/group of devices NEMO SX
Name of the Gateway and Modbus address of the device/group of devices NEMO SX in which the event occurred
Type of alarm/event: e.g. Tripped, Duplicated function, Communication error, …
1

## Slide 113
8.7 System information
“System information" page allows the user to have information relating to the operation of the Web Server such as:
- Firmware version installed
- Date and Time of the last restart
- System resources allocated
- Storage space allocated and Integrity of the database
- …
Access to the page
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “System information”
2
1

## Slide 114
System information page appears
The page contains following information:
Firmware version installed
Date and Time of the last restart of the hardware
Date and Time of the last restart of the application embedded on the hardware
Percentage of CPU used. A consistently high value (> 80%) can indicate some hardware problems
Information about the Database saved in the Web server: - Database size
- Available storage space for the Database
- Date and time of the Database Backup performed by the Web server Note: this Backup is different from the one created by the user with the “Backup” function, as describe in the next chapter of this manual.
- Status of the Database Backup: “Ok” or “Error” (in case of error contact technical support)
- Database Health status: informs the user on the necessity to optimise the internal Database of the Web Server. If the database becomes too large, performances of the Web Server will deteriorate and there is the risk of errors in histograms displaying and in the saving of data. Consequently, it is suggested to optimize the Web Server database via the “Optimize” button that appears in the lower part of the page.
To perform the optimization of the Database, 3. Click “Optimize”.
C
D
A
B
A
B
C
D
3

## Slide 115
9 Backup and Restore
These procedures are used to create a backup of the device configuration and to perform the restore of a saved configuration.
9.1 Backup procedure
In the Web Server’s home page
1. Click “Web Server configuration”
2. Click “Backup/Restore”
1
2

## Slide 116
Backup and restore page appears
3. Click “Backup” to access the page
4. Click “Backup” to perform the function.
A file named “database.zip” is automatically saved on the HDD of the web server.
It’s possible to save in local the file by accessing to the HDD via FTP or Network drive (see § 8.3.2)
Note: not modify the zip folder’s name and its contents to avoid problems during the restore procedure! (names and types of files, etc..)
3
4

## Slide 117
9.2 Restore procedure
1. Copy the file to restore “database.zip” in the Web server’s FTP
In the Web Server’s home page
2. Click “Web Server configuration”
3. Click “Backup/Restore”
2
3

## Slide 118
Backup and restore page appears
4. Click “Restore” to access the page
5. Click “Restore” to perform the function.
Note: the good result of the operation will be guaranteed only if the folder’s name and its contents has not been modified after the backup (names and types of files, etc..).
3
4

## Slide 119
10. Network type and access mode 10.1 LAN/intranet
Private network
Addresses and rights managed by the Manager of the Building
10.1.1 Ports
Web Server to Gateways or to Slave Web servers:
Port 502, Modbus TCP
IP1
Hub/Switch
Hub/Switch
IP2
Hub/Switch
LAN/ Intranet
IP3
Hub/Switch
Hub/Switch

## Slide 120
Users to Web Server:
Port 80, HTTP (http://IP2 by web browser)
Port 443, HTTPS (https://IP2 by web browser)
Port 443, Telegram
Ports 20 and 21, FTP (ftp://IP2 by web browser or in “My Computer”)
10.2 WAN/Internet
Public network
Fixed* IP Box: the IP address remains the same
 Access by IP address (Fixed IP paying according to the operators)
Dynamic* IP Box: the address may change
 Access by Name (possibility of creating a dynamic DNS account – Example www.dyndns.org).
User: access by the public address of the Box (IP/Name, Internet)
Web Server: always has a fixed private address (IP2, Intranet)
 It is necessary to achieve the association web server/Box*
* More information from the ADSL operator
Hub/Switch
Hub/Switch
IP2
Hub/Switch
Box ADSL
IP2
Hub/Switch
IP/Name
IP3
WAN/ Internet

## Slide 121
10.2.1 Ports
Web Server to Gateway:
Port 502, Modbus TCP
Users to Web Server:
Port 80, HTTP (http://IP2 by web browser)
Port 443, HTTPS (https://IP2 by web browser)
Ports 20 and 21, FTP (ftp://IP2 by web browser or in “My Computer”)
IP (fixed)
Name (dynamic IP)
IP2
Box ADSL
Hub/Switch
Hub/Switch

## Slide 122
11. FAQ
11.1 Access problems
If typing the PIN and PUK codes, Web Server’s home page is not displayed correctly (continuous refresh of the page), you have to do the following operations :
delete the cookies
delete the internet temporary files
delete the cache
delete the chronology
11.2 Telegram problems
If the “Test” function in the Telegram page does not work correctly, you have to check:
the correct opening of the communication port 443 (see § 10.1.1)
the correct configuration of the DNS of the Web server in the “Network settings” page (see § 7.5.1)
11.3 E-mails sending test problems
If the “Test” function in the e-mails sender configuration page (page “Email“ in the “Email and notification“ menu) does not work correctly, you have to check:
the correct opening of the communication port configured in the menu
the correct configuration of the DNS of the Mini Web server in the “Network settings” page (see § 7.5.1)
Options of your e-mail account related to access by deemed less secure applications

## Slide 128
IME reserves at any time the right to modify the contents of this booklet and to communicate in any
form and modality, the changes brought to the same.
BTicino SpA
Viale Borri, 231
21100 Varese - Italy
www.imeitaly.com